## Block Load
HVAC QUICK LOAD PROGRAM
COMPANY: | [5 empty] | DATE: | 2021-06-24 18:28
PROJECT: | [5 empty] | PROJ. NO.:
AHU # | MONTH | TIME | OUTDOOR AIR TEMPERATURES |  |  | INDOOR AIR TEMP
| (1-12) | (7am-6pm) | SUMMER |  | WINTER | RH = | 49.98%
AHU-1 | hqlp | 5 | 94 | 74 | 12 | 72 | 60.08
AHU TYPE |  | HOURS OF | "U" VALUES |  |  | GLASS SAFETY FACTORS
BLOWTHRU = BT |  | 0PERATION
DRAWTHRU = DT |  | (12, 16, 24) | WALL | ROOF | GLASS | BARE | SHADED
DT |  | 24 | 0.1 | 0.08 | 1.13 | 0.8 | 0.65
GLASS SOLAR HEAT GAIN
INT SHADE ? | EXPOSURE | AREA | PEAK SOLAR HEAT GAIN | 24 HR STORAGE | SHADE FACTOR | SAFETY FACTOR | BTU/HR
(Y/N) |  | (SQ.FT.)
N | N | 100 | 0 | 0.8 | 0.8 | 1.1 | 0
N | S | 100 | 4 | 0.45 | 0.8 | 1.1 | 158.4
N | E | 100 | 2 | 0.2 | 0.8 | 1.1 | 35.2
N | W | 100 | 6 | 0.48 | 0.8 | 1.1 | 253.44
N | NE | 100 | 1 | 0.17 | 0.8 | 1.1 | 14.96
N | NW | 100 | 7 | 0.4 | 0.8 | 1.1 | 246.4
N | SE | 100 | 3 | 0.27 | 0.8 | 1.1 | 71.28
N | SW | 100 | 5 | 0.51 | 0.8 | 1.1 | 224.4
SKYLIGHT | HORIZ. | 100 | 8 | 1 | 1 | 1.1 | 880
SUB-TOTAL = | [6 empty] | 1884.08
TRANSMISSION HEAT GAIN
| EXPOSURE | AREA | EQUIVALENT TEMP. DIFF. | TEMP. CORRECTION | "U" VALUE | SAFETY FACTOR | BTU/HR
(SQ.FT.)
WALL: | N | 100 | 11 | 10 | 0.1 | 1.1 | 231
WALL: | S | 100 | 23 | 10 | 0.1 | 1.1 | 363
WALL: | E | 100 | 13 | 10 | 0.1 | 1.1 | 253
WALL: | W | 100 | 34 | 10 | 0.1 | 1.1 | 484
WALL: | NE | 100 | 13 | 10 | 0.1 | 1.1 | 253
WALL: | NW | 100 | 21 | 10 | 0.1 | 1.1 | 341
WALL: | SE | 100 | 15 | 10 | 0.1 | 1.1 | 275
WALL: | SW | 100 | 35 | 10 | 0.1 | 1.1 | 495
ROOF: | HORIZ. | 100 | 43 | 10 | 0.04 | 1.1 | 233.2
GLASS: |  | 900 | 22 |  | 1.13 | 1.1 | 24611.4
PARTITION: |  | 100 | 10 |  | 0.2 | 1.1 | 220
SUB-TOTAL = | [6 empty] | 27759.6
INTERNAL HEAT GAIN
|  | QUANTITY OR SQ.FT. | WATTS PER SQ.FT. | CONVERT FACTOR | MULTIPLIER FACTOR | SAFETY FACTOR | BTU/HR
NO. OF PEOPLE: |  | 10 | 250 |  |  | 1.1 | 2750
FLUOR. LIGHTS (SF): |  | 1000 | 2 | 3.413 | 80% | 1.1 | 6006.88
INCAN. LIGHTS (SF): |  | 1000 | 0.25 | 3.413 | 100% | 1.1 | 938.575
POWER (SF): |  | 1000 | 2 | 3.413 | 100% | 1.1 | 7508.6
EQUIPMENT (SF): |  | 1000 | 2 | 3.413 | 100% | 1.1 | 7508.6
INFILTRATION SENSIBLE: |  | 100 | 22 |  | 1.0845 | 1.1 | 2624.49
SUB-TOTAL = | [6 empty] | 27337.145
ROOM SENSIBLE HEAT GAIN
TOTAL STATIC = |  | 2 |  | ROOM SENSIBLE HEAT (BTU/HR)= |  |  | 56980.825
AIRFLOW @ |  | 20 |  | 2627.0551
MOTOR SIZE = |  | 1.3777
MOTOR HEAT RISE = |  | 1.2307 |  | HEAT GAIN FROM MOTOR (BTH/HR) = |  |  | 3506.3222
SUB-TOTAL = | [6 empty] | 60487.1472
RETURN AIR HEAT GAIN
| EXPOSURE | AREA | EQUIVALENT TEMP. DIFF. | TEMP. CORRECTION | "U" VALUE | SAFETY FACTOR | BTU/HR
(SQ.FT.)
WALL: | N | 10 | 11 | 10 | 0.1 | 1.1 | 23.1
WALL: | S | 10 | 23 | 10 | 0.1 | 1.1 | 36.3
WALL: | E | 10 | 13 | 10 | 0.1 | 1.1 | 25.3
WALL: | W | 10 | 34 | 10 | 0.1 | 1.1 | 48.4
WALL: | NE | 10 | 13 | 10 | 0.1 | 1.1 | 25.3
WALL: | NW | 10 | 21 | 10 | 0.1 | 1.1 | 34.1
WALL: | SE | 10 | 15 | 10 | 0.1 | 1.1 | 27.5
WALL: | SW | 10 | 35 | 10 | 0.1 | 1.1 | 49.5
ROOF: | HORIZ. | 100 | 43 | 10 | 0.04 | 1.1 | 233.2
LIGHTS: | (FLUOR.) | 1000 | 2 | 3.413 | 20% | 1.1 | 1501.72
MOTOR BHP: |  | 1.3777 |  | HEAT GAIN FROM MOTOR = |  |  | 0
SUB-TOTAL = | [6 empty] | 2004.42
OUTSIDE AIR HEAT GAIN
|  | CFM PER PERSON | CFM | TEMP. DIFFERENCE | MULTIPLIER FACTOR | SAFETY FACTOR | BTU/HR
O/A SENSIBLE: |  | 375 | 3750 | 22 | 1.0845 | 1.1 | 98418.375
GRAND TOTAL SENSIBLE HEAT (BTU/HR) = | [6 empty] | 160909.9422
LATENT HEAT GAIN
|  |  | CFM OUTSIDE AIR | DELTA GRAINS | MULTIPLIER FACTOR | SAFETY FACTOR | BTU/HR
OUTSIDE AIR LATENT: |  |  | 3750 | 35.7709 | 0.68 | 1.1 | 100337.4379
INFILTRATION LATENT: |  |  | 100 | 35.7709 | 0.68 | 1.1 | 2675.665
PEOPLE LATENT: |  | 10 | 200 |  |  | 1.1 | 2200
SUB-TOTAL = | [6 empty] | 105213.1029
GRAND TOTAL LATENT HEAT (BTH/HR) = | [6 empty] | 105213.1029
ROOM SENSIBLE HEAT RATIO = |  |  | 0.96491 | GRAND TOTAL HEAT (BTU/HR) = |  |  | 266123.0451
TOTAL SENSIBLE HEAT RATIO = |  |  | 0.60464 | TONNAGE = |  |  | 22.1769
ENTERING ENTHALPY = |  |  | 42.9225 | ENTERING AIR TEMPERATURE = |  |  | 103.404
LEAVING ENTHALPY = |  |  | 20.4112 | LEAVING AIR TEMPERATURE = |  |  | 50.7693
TRANSMISSION HEAT LOSS
|  | EXPOSURE | AREA | EQUIVALENT TEMP. DIFF. | "U" VALUE | SAFETY FACTOR | BTU/HR
(SQ.FT.)
| WALL: | N | 100 | 60 | 0.1 | 1.2 | 720
| WALL: | S | 100 | 60 | 0.1 | 1.2 | 720
| WALL: | E | 100 | 60 | 0.1 | 1.2 | 720
| WALL: | W | 100 | 60 | 0.1 | 1.2 | 720
| ROOF: | INCLUDED IN PLENUM HEAT
| GLASS: |  | 900 | 60 | 1.13 | 1.2 | 73224
| PARTITION: |  | 100 | 60 | 0.2 | 1.2 | 1440
| SUB-TOTAL = | [5 empty] | 77544
INTERNAL HEAT LOSS
|  |  |  | CFM | TEMP. DIFFERENCE | MULTIPLIER FACTOR | BTU/HR
| INFILTRATION SENSIBLE: |  |  | 100 | 60 | 1.0845 | 6507
| SUBTOTAL = | [5 empty] | 6507
ROOM SENSIBLE HEAT GAIN
| TOTAL STATIC = |  | 2 | ROOM SENSIBLE HEAT (BTU/HR)= |  |  | 84051
| AIRFLOW @ |  | 20 |  | 2627.0551
| MOTOR SIZE = |  | 1.3777
| MOTOR HEAT RISE = |  | 1.2307 | HEAT GAIN FROM MOTOR (BTH/HR) = |  |  | -3506.3222
| SUB-TOTAL = | [5 empty] | 80544.6778
RETURN AIR HEAT LOSS
|  | EXPOSURE | AREA | TEMP. DIFFERENCE | "U" VALUE | SAFETY FACTOR | BTU/HR
(SQ.FT.)
| WALL: | N | 10 | 60 | 0.1 | 1.2 | 72
| WALL: | S | 10 | 60 | 0.1 | 1.2 | 72
| WALL: | E | 10 | 60 | 0.1 | 1.2 | 72
| WALL: | W | 10 | 60 | 0.1 | 1.2 | 72
| ROOF: | HORIZ. | 100 | 60 | 0.08 | 1.2 | 576
| LIGHTS: | (FLUOR.) | 1000 | 2 | 3.413 | 20% | 1365.2
| MOTOR BHP: |  | 1.3777 | HEAT GAIN FROM MOTOR = |  |  | 0
| SUB-TOTAL = | [5 empty] | 2229.2
OUTSIDE AIR HEAT LOSS
|  |  | CFM | TEMP. DIFFERENCE | MULTIPLIER FACTOR | SAFETY FACTOR | BTU/HR
| OUTSIDE AIR: |  | 3750 | 60 | 1.0845 | 1.2 | 292815
| GRAND TOTAL LOSS (BTU/HR) = | [5 empty] | 292815
OUTSIDE AIR CONDITIONS | [5 empty] | INSIDE AIR CONDITIONS | [5 empty] | LEAVING COIL CONDITIONS
TEMPDB | 94 | TEMPWB | 74 |  |  | TEMPDB | 72 | TEMPWB | 60.08 |  |  | TEMPDB | 50.7693 | TEMPWB | 50.2693
TEMPK | 307.6044 | TEMPK | 296.4933 |  |  | TEMPK | 295.3822 | TEMPK | 288.76 |  |  | TEMPK | 283.5874 | TEMPK | 283.3096
AA | 0.88802 | AA | 0.9213 | 2723.44 |  | AA | 0.92477 | AA | 0.94598 | 2743.4848 |  | AA | 0.96323 | AA | 0.96417 | 2757.6122
BB | 0.11198 | BB | 0.078698 |  |  | BB | 0.075232 | BB | 0.054024 |  |  | BB | 0.03677 | BB | 0.035825
CC | 0.1261 | CC | 0.08542 |  |  | CC | 0.081352 | CC | 0.057109 |  |  | CC | 0.038173 | CC | 0.037156
DD | 1.2089 | DD | 0.84961 |  |  | DD | 0.8122 | DD | 0.58324 |  |  | DD | 0.39696 | DD | 0.38676
FNGOFF | 0.79137 | FNGOFF | 0.41589 |  |  | FNGOFF | 0.3888 | FNGOFF | 0.25707 |  |  | FNGOFF | 0.18327 | FNGOFF | 0.1799
PSATDB | 0.79137 | PSATWB | 0.41589 |  |  | PSATDB | 0.3888 | PSATWB | 0.25707 |  |  | PSATDB | 0.18327 | PSATWB | 0.1799
|  | PPWV | 0.31099 |  |  |  |  | PPWV | 0.19432 |  |  |  |  | PPWV | 0.17727
|  | FNRH | 39.2981 |  |  |  |  | FNRH | 49.9799 |  |  |  |  | FNRH | 96.7238
|  | WLB | 0.013441 |  |  |  |  | WLB | 0.008331 |  |  |  |  | WLB | 0.0075909
|  | WGR | 94.0877 |  |  |  |  | WGR | 58.3168 |  |  |  |  | WGR | 53.1363
|  | VOLDA | 13.9631 |  |  |  |  | VOLDA | 13.4086 |  |  |  |  | VOLDA | 12.8735
|  | VOLMX | 14.2648 |  |  |  |  | VOLMX | 13.5882 |  |  |  |  | VOLMX | 13.0306
|  | FNENTH | 37.3847 |  |  |  |  | FNENTH | 26.3871 |  |  |  |  | FNENTH | 20.4112
OUTSIDE AIR DRY BULB TEMPERATURES
|  | PM | PM | PM | PM | PM | PM | AM | AM | AM | AM | AM | NOON
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
JAN | 1 | 77 | 79 | 80 | 79 | 78 | 78 | 67 | 68 | 69 | 71 | 73 | 75
FEB | 2 | 77 | 79 | 80 | 79 | 78 | 78 | 67 | 68 | 69 | 71 | 73 | 75
MAR | 3 | 77 | 79 | 80 | 79 | 78 | 78 | 67 | 68 | 69 | 71 | 73 | 75
APR | 4 | 81 | 83 | 84 | 83 | 82 | 82 | 71 | 72 | 73 | 75 | 77 | 79
MAY | 5 | 89 | 91 | 92 | 91 | 90 | 90 | 79 | 80 | 81 | 83 | 85 | 87
JUN | 6 | 94 | 96 | 96 | 96 | 95 | 95 | 84 | 85 | 86 | 88 | 90 | 92
JUL | 7 | 96 | 96 | 96 | 96 | 96 | 98 | 87 | 88 | 89 | 91 | 93 | 95
AUG | 8 | 96 | 96 | 96 | 96 | 96 | 98 | 87 | 88 | 89 | 91 | 93 | 92
SEP | 9 | 93 | 95 | 96 | 95 | 94 | 94 | 83 | 84 | 85 | 87 | 89 | 91
OCT | 10 | 85 | 87 | 88 | 87 | 86 | 86 | 75 | 76 | 77 | 79 | 81 | 83
NOV | 11 | 77 | 79 | 80 | 79 | 78 | 78 | 67 | 68 | 69 | 71 | 73 | 75
DEC | 12 | 77 | 79 | 80 | 79 | 78 | 78 | 67 | 68 | 69 | 71 | 73 | 75
OUTSIDE AIR W.B. TEMPERATURES
|  | PM | PM | PM | PM | PM | PM | AM | AM | AM | AM | AM | NOON
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
JAN | 1 | 69 | 69 | 69 | 69 | 69 | 68 | 65 | 66 | 66 | 67 | 67 | 68
FEB | 2 | 69 | 69 | 69 | 69 | 69 | 68 | 65 | 66 | 66 | 67 | 67 | 68
MAR | 3 | 69 | 69 | 69 | 69 | 69 | 68 | 65 | 66 | 66 | 67 | 67 | 68
APR | 4 | 71 | 71 | 71 | 71 | 71 | 70 | 67 | 68 | 68 | 69 | 69 | 70
MAY | 5 | 76 | 76 | 76 | 76 | 76 | 75 | 73 | 73 | 73 | 74 | 74 | 75
JUN | 6 | 78 | 78 | 78 | 78 | 78 | 77 | 75 | 75 | 75 | 76 | 76 | 77
JUL | 7 | 80 | 80 | 80 | 80 | 80 | 79 | 77 | 77 | 77 | 78 | 78 | 79
AUG | 8 | 80 | 80 | 80 | 80 | 80 | 79 | 77 | 77 | 77 | 78 | 78 | 79
SEP | 9 | 78 | 78 | 78 | 78 | 78 | 77 | 75 | 75 | 75 | 76 | 76 | 77
OCT | 10 | 74 | 74 | 74 | 74 | 74 | 73 | 70 | 71 | 71 | 72 | 72 | 73
NOV | 11 | 69 | 69 | 69 | 69 | 69 | 68 | 65 | 66 | 66 | 67 | 67 | 68
DEC | 12 | 69 | 69 | 69 | 69 | 69 | 68 | 65 | 66 | 66 | 67 | 67 | 68
GRAINS OF WATER PER POUND OF DRY AIR AT OUTSIDE AIR DESIGN CONDITIONS
|  | PM | PM | PM | PM | PM | PM | AM | AM | AM | AM | AM | NOON
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
JAN | 1 | 94 | 90 | 89 | 90 | 92 | 87 | 90 | 93 | 91 | 93 | 90 | 92
FEB | 2 | 94 | 90 | 89 | 90 | 92 | 87 | 90 | 93 | 91 | 93 | 90 | 92
MAR | 3 | 94 | 90 | 89 | 90 | 92 | 87 | 90 | 93 | 91 | 93 | 90 | 92
APR | 4 | 98 | 95 | 93 | 95 | 97 | 91 | 93 | 97 | 95 | 97 | 94 | 96
MAY | 5 | 115 | 111 | 110 | 118 | 113 | 116 | 113 | 111 | 110 | 113 | 109 | 112
JUN | 6 | 119 | 116 | 116 | 116 | 118 | 111 | 117 | 115 | 113 | 116 | 113 | 116
JUL | 7 | 129 | 129 | 129 | 129 | 129 | 123 | 124 | 123 | 121 | 124 | 121 | 124
AUG | 8 | 129 | 129 | 129 | 129 | 129 | 123 | 124 | 123 | 121 | 124 | 121 | 124
SEP | 9 | 121 | 118 | 116 | 118 | 119 | 113 | 119 | 117 | 115 | 118 | 115 | 118
OCT | 10 | 109 | 106 | 104 | 106 | 107 | 101 | 102 | 106 | 105 | 107 | 104 | 106
NOV | 11 | 94 | 90 | 89 | 90 | 92 | 87 | 90 | 93 | 91 | 93 | 90 | 92
DEC | 12 | 94 | 90 | 89 | 90 | 92 | 87 | 90 | 93 | 91 | 93 | 90 | 92
EQUIVALENT TEMPERATURE DIFFERENCE (60 LB/SQ.FT. WALL AND 20 LB/SQ.FT. ROOF CONSTRUCTION)
| PM | PM | PM | PM | PM | PM | AM | AM | AM | AM | AM | NOON
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 15 | 10 | 11 | 12 | 13 | 14 | -2 | -2 | 5 | 24 | 22 | 20
E | 19 | 14 | 13 | 12 | 13 | 14 | -1 | 0 | 21 | 30 | 31 | 31
SE | 26 | 25 | 21 | 18 | 15 | 14 | 1 | 0 | 13 | 20 | 24 | 28
S | 20 | 24 | 25 | 26 | 23 | 20 | -3 | -4 | -3 | -2 | 7 | 12
SW | 8 | 12 | 24 | 32 | 35 | 36 | 1 | 0 | 0 | 0 | 1 | 2
W | 7 | 10 | 19 | 26 | 34 | 40 | 1 | 0 | 0 | 0 | 2 | 4
NW | 6 | 8 | 10 | 12 | 21 | 30 | -3 | -4 | -3 | -2 | 0 | 2
N | 3 | 6 | 8 | 10 | 11 | 12 | -3 | -4 | -3 | -2 | -1 | 0
HORIZ. | 23 | 30 | 36 | 41 | 43 | 43 | -1 | -2 | -1 | 2 | 9 | 16
PEAK SOLAR HEAT GAIN FACTORS
|  | N | NE | E | SE | S | SW | W | NW | HORIZ.
JAN | 1 | 23 | 29 | 172 | 244 | 243 | 244 | 172 | 29 | 175
FEB | 2 | 28 | 63 | 195 | 239 | 214 | 239 | 195 | 63 | 213
MAR | 3 | 32 | 103 | 215 | 218 | 171 | 218 | 215 | 103 | 244
APR | 4 | 37 | 141 | 219 | 180 | 111 | 180 | 219 | 141 | 225
MAY | 5 | 40 | 167 | 216 | 150 | 71 | 150 | 216 | 167 | 273
JUN | 6 | 46 | 176 | 214 | 139 | 60 | 139 | 214 | 176 | 276
JUL | 7 | 40 | 167 | 216 | 150 | 71 | 150 | 216 | 167 | 273
AUG | 8 | 37 | 141 | 219 | 180 | 111 | 180 | 219 | 141 | 225
SEP | 9 | 32 | 103 | 215 | 218 | 171 | 218 | 215 | 103 | 244
OCT | 10 | 28 | 63 | 195 | 239 | 214 | 239 | 195 | 63 | 213
NOV | 11 | 23 | 29 | 172 | 244 | 243 | 244 | 172 | 29 | 175
DEC | 12 | 21 | 21 | 162 | 246 | 254 | 246 | 162 | 21 | 158
STORAGE LOAD FACTORS, 12 HOUR OPERATION, INTERNAL SHADE (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.23 | 0.2 | 0.19 | 0.17 | 0.15 | 0.59 | 0.68 | 0.64 | 0.52 | 0.35 | 0.29 | 0.24
E | 0.26 | 0.24 | 0.21 | 0.19 | 0.16 | 0.52 | 0.67 | 0.73 | 0.7 | 0.58 | 0.4 | 0.29
SE | 0.49 | 0.34 | 0.28 | 0.25 | 0.21 | 0.18 | 0.4 | 0.57 | 0.7 | 0.75 | 0.72 | 0.63
S | 0.79 | 0.77 | 0.65 | 0.51 | 0.31 | 0.26 | 0.22 | 0.38 | 0.51 | 0.64 | 0.73 | 0.79
SW | 0.64 | 0.74 | 0.77 | 0.7 | 0.55 | 0.33 | 0.28 | 0.25 | 0.23 | 0.23 | 0.35 | 0.5
W | 0.28 | 0.44 | 0.61 | 0.72 | 0.73 | 0.67 | 0.33 | 0.28 | 0.26 | 0.24 | 0.22 | 0.2
NW | 0.18 | 0.23 | 0.4 | 0.58 | 0.7 | 0.71 | 0.31 | 0.27 | 0.24 | 0.22 | 0.21 | 0.19
N | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
STORAGE LOAD FACTORS, 12 HOUR OPERATION, BARE GLASS (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.3 | 0.27 | 0.26 | 0.23 | 0.2 |  | 0.45 | 0.5 | 0.49 | 0.45 | 0.42 | 0.34
E | 0.39 | 0.34 | 0.31 | 0.28 | 0.24 |  | 0.44 | 0.54 | 0.58 | 0.57 | 0.51 | 0.44
SE | 0.56 | 0.49 | 0.44 | 0.37 | 0.33 |  | 0.33 | 0.41 | 0.51 | 0.58 | 0.61 | 0.61
S | 0.68 | 0.7 | 0.68 | 0.63 | 0.53 |  | 0.37 | 0.39 | 0.43 | 0.5 | 0.57 | 0.64
SW | 0.46 | 0.55 | 0.62 | 0.64 | 0.6 |  | 0.44 | 0.37 | 0.35 | 0.31 | 0.33 | 0.39
W | 0.28 | 0.33 | 0.43 | 0.51 | 0.57 |  | 0.52 | 0.44 | 0.39 | 0.34 | 0.31 | 0.29
NW | 0.23 | 0.24 | 0.3 | 0.39 | 0.48 |  | 0.49 | 0.41 | 0.35 | 0.31 | 0.28 | 0.25
N | 0.94 | 0.94 | 0.95 | 0.95 | 0.95 |  | 0.84 | 0.86 | 0.89 | 0.91 | 0.93 | 0.93
STORAGE LOAD FACTORS, 16 HOUR OPERATION, INTERNAL SHADE (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.21 | 0.17 | 0.16 | 0.15 | 0.13 | 0.11 | 0.65 | 0.61 | 0.5 | 0.33 | 0.27 | 0.22
E | 0.24 | 0.2 | 0.18 | 0.16 | 0.14 | 0.12 | 0.63 | 0.7 | 0.67 | 0.56 | 0.38 | 0.27
SE | 0.47 | 0.29 | 0.24 | 0.21 | 0.18 | 0.15 | 0.35 | 0.53 | 0.66 | 0.72 | 0.69 | 0.61
S | 0.7 | 0.69 | 0.59 | 0.45 | 0.26 | 0.22 | 0.14 | 0.31 | 0.46 | 0.59 | 0.69 | 0.76
SW | 0.6 | 0.66 | 0.7 | 0.64 | 0.5 | 0.26 | 0.19 | 0.18 | 0.17 | 0.18 | 0.31 | 0.46
W | 0.23 | 0.36 | 0.54 | 0.66 | 0.68 | 0.6 | 0.21 | 0.19 | 0.19 | 0.17 | 0.16 | 0.15
NW | 0.15 | 0.16 | 0.34 | 0.52 | 0.65 | 0.23 | 0.19 | 0.18 | 0.17 | 0.17 | 0.16 | 0.16
N | 0.84 | 0.85 | 0.87 | 0.88 | 0.89 | 0.9 | 0.46 | 0.73 | 0.78 | 0.82 | 0.82 | 0.83
STORAGE LOAD FACTORS, 16 HOUR OPERATION, BARE GLASS (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.27 | 0.22 | 0.21 | 0.19 | 0.17 | 0.16 | 0.39 | 0.45 | 0.45 | 0.41 | 0.39 | 0.31
E | 0.35 | 0.28 | 0.25 | 0.23 | 0.2 | 0.18 | 0.38 | 0.48 | 0.54 | 0.52 | 0.48 | 0.41
SE | 0.53 | 0.41 | 0.36 | 0.31 | 0.27 | 0.24 | 0.24 | 0.33 | 0.44 | 0.52 | 0.57 | 0.57
S | 0.6 | 0.6 | 0.57 | 0.53 | 0.45 | 0.37 | 0.24 | 0.28 | 0.34 | 0.42 | 0.5 | 0.58
SW | 0.4 | 0.46 | 0.5 | 0.53 | 0.51 | 0.44 | 0.28 | 0.25 | 0.24 | 0.22 | 0.26 | 0.33
W | 0.21 | 0.23 | 0.3 | 0.4 | 0.48 | 0.51 | 0.31 | 0.28 | 0.25 | 0.23 | 0.22 | 0.21
NW | 0.17 | 0.17 | 0.19 | 0.29 | 0.4 | 0.46 | 0.28 | 0.25 | 0.23 | 0.22 | 0.2 | 0.19
N | 0.78 | 0.79 | 0.8 | 0.81 | 0.82 | 0.83 | 0.47 | 0.6 | 0.67 | 0.72 | 0.74 | 0.77
STORAGE LOAD FACTORS, 24 HOUR OPERATION, INTERNAL SHADE (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.19 | 0.17 | 0.16 | 0.15 | 0.13 | 0.11 | 0.6 | 0.57 | 0.46 | 0.3 | 0.24 | 0.2
E | 0.22 | 0.2 | 0.18 | 0.16 | 0.14 | 0.12 | 0.58 | 0.65 | 0.63 | 0.52 | 0.35 | 0.24
SE | 0.44 | 0.29 | 0.24 | 0.21 | 0.18 | 0.15 | 0.28 | 0.47 | 0.61 | 0.67 | 0.65 | 0.57
S | 0.71 | 0.69 | 0.59 | 0.45 | 0.26 | 0.22 | 0.04 | 0.22 | 0.38 | 0.52 | 0.63 | 0.7
SW | 0.55 | 0.66 | 0.7 | 0.64 | 0.5 | 0.26 | 0.08 | 0.08 | 0.08 | 0.1 | 0.24 | 0.4
W | 0.18 | 0.36 | 0.54 | 0.66 | 0.68 | 0.6 | 0.08 | 0.08 | 0.09 | 0.09 | 0.09 | 0.09
NW | 0.1 | 0.16 | 0.34 | 0.52 | 0.65 | 0.64 | 0.08 | 0.09 | 0.09 | 0.1 | 0.1 | 0.1
N | 0.83 | 0.85 | 0.87 | 0.88 | 0.9 | 0.91 | 0.31 | 0.67 | 0.72 | 0.76 | 0.79 | 0.81
STORAGE LOAD FACTORS, 24 HOUR OPERATION, BARE GLASS (100 LB/SQ.FT. WALL CONSTRUCTION)
| PM | [8 empty] | AM | AM | NOON | bar: N to NW
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
NE | 0.24 | 0.22 | 0.21 | 0.19 | 0.17 | 0.16 | 0.31 | 0.38 | 0.39 | 0.36 | 0.34 | 0.27
E | 0.31 | 0.28 | 0.25 | 0.23 | 0.2 | 0.18 | 0.29 | 0.4 | 0.46 | 0.46 | 0.42 | 0.36
SE | 0.47 | 0.41 | 0.36 | 0.31 | 0.27 | 0.24 | 0.12 | 0.23 | 0.35 | 0.44 | 0.49 | 0.51
S | 0.54 | 0.58 | 0.57 | 0.53 | 0.45 | 0.37 | 0.06 | 0.12 | 0.2 | 0.3 | 0.39 | 0.48
SW | 0.31 | 0.42 | 0.5 | 0.53 | 0.51 | 0.44 | 0.09 | 0.08 | 0.09 | 0.09 | 0.14 | 0.22
W | 0.12 | 0.19 | 0.3 | 0.4 | 0.48 | 0.51 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.1
NW | 0.09 | 0.11 | 0.19 | 0.29 | 0.4 | 0.46 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
N | 0.7 | 0.74 | 0.76 | 0.79 | 0.8 | 0.6 | 0.33 | 0.44 | 0.51 | 0.57 | 0.62 | 0.66

## Instructions
Instructions for using the HVAC Quick Load Program
1 | Information is required anywhere "red" text is shown or there is a yellow-highlighted cell.
2 | Fill in your company name/your name, the project name and project number (if appropriate.)
3 | The date autofills with the current day.
4 | Once all the other inputs are in, you run through the months (i.e. 1 through 12) to get the highest sensible and total load. Then, leaving the month alone, run through the times (i.e. 7, 8, 9, 19, 11, 12, 1, 2, 3, 4, 5, 6) to see which one returns the highest sensible and total load.
5 | Also, try different combinations of Indoor Air dry bulb and wet bulb to get your required Indoor Air Relative Humidity. I have shown 72°F/60.08°F to get a resulting 50%RH.
6 | In the Hours of Operation block only use "12", "16", or "24" for the input.
7 | Int. Shade? denotes internal shading. If you are certain the building will have (and use) internal shading devices, then put a "Y" in the cell. Otherwise leave the "N".
8 | For the "Exposures", the only inputs you can use are "N", "S", "E", "W", "NE", "SE", "SW", & "NW". Future updates will have more options.
9 | Run through the program a few times to get a "feel" for how it works. If you find anything that is not working like it should, let me know. Also, if you want to make suggestions to improve the "use-ability" of this quick load program, please do so. I would like to refine this product and update accordingly.